## Slide 1
物聯網實作 使用Raspberry Pi+Power Meter
1
Yungchun-Wen
Notes: 1

## Slide 2
INDEX
2
Abstract
Power Meter配置圖
Modbus工業通信協定標準
NODE RED程式設計
習題
Reference
Notes: 2

## Slide 3
Abstract
3
為實現簡易的物聯網實驗,以Power Meter為例,規劃以下感測器資訊收集平台:
採用RASPBERRY PI3平台,對外INTERNET通訊使用WI-FI,對家庭內的感測器通訊使用ZIGBEE無線電通訊
Power Meter每日收集室內插座用電資訊,在Node RED Dashboard將電源數據圖表可視化
Notes: 3

## Slide 4
4
Raspberry Pi+Power Meter架構圖
Power Meter
RS485
ZIGBEE End Device
網際網路
電腦
ZIGBEE Coordinator
Notes: 4

## Slide 5
5
今日需安裝的軟體:
電腦安裝,DIGI XCTU,NODE-RED,REAL VNC,WIN-SCP
MODBUS RTU
http://ebook.yourplc.net/modules/wfdownloads/singlefile.php?cid=11&lid=103
Notes: 5

## Slide 6
6
準備工具:
小一字起
AC插頭電線
16AWG (或1.25mm) 電線長度60CM
24AWG(或0.5mm)電線長度100CM
電氣絕緣膠帶一捲
電烙鐵一支
焊錫20CM
電源插頭3PIN轉接2PIN.
斜口鉗
數位電錶(非必要,若有可攜帶)
Notes: 6

## Slide 7
7
Notes: 7

## Slide 8
Power Meter配置圖
8
Notes: 8

## Slide 9
9
PZEM-016為AC電壓電流感測模組,RS485傳輸介面
https://www.taiwansensor.com.tw/product/%E5%96%AE%E7%9B%B8%E4%BA%A4%
E6%B5%81%E9%9B%BB%E6%99%BA%E6%85%A7%E9%9B%BB%E9%87%8F%E7%9B%A3%E6
%8E%A7%E5%99%A8-%E7%9B%A3%E6%8E%A7%E9%9B%BB%E5%A3%93%E9%9B%BB%E6
%B5%81%E9%9B%BB%E9%87%8F%E5%8A%9F/

## Slide 10
10
Power Meter
Raspberry pi
MODBUS
RS485
通訊架構
Master device
Slave device

## Slide 11
11
參考 https://www.youtube.com/watch?v=74gKMTsHmYY
規格書 https://images-na.ssl-images-amazon.com/images/I/81GtkIOyZaL.pdf
Notes: 11

## Slide 12
12
注意:
端子的螺絲鎖緊後,用手拉一拉確認無鬆脫,以免掉落.
配線方式可參考下圖,配線花費時間大約1.5小時完成.
若無接線能力可請同學互相幫忙焊接,或請助教幫忙確認,
特別是AC 110V INPUT的部分很危險.
PZEM-16必須在AC110V插著電才會工作.
PZEM-16 5V是輸出電源,輸出電流小,不可以輸入其他電壓
Notes: 12

## Slide 13
13
Notes: 13

## Slide 14
14
配線實照:
Notes: 14

## Slide 15
15
Notes: 15

## Slide 16
16
Notes: 16

## Slide 17
17
Notes: 17

## Slide 18
Modbus工業通信協定標準
18
Notes: 18

## Slide 19
Modbus通訊可架構在不同PHY層上.
可參考https://zh.wikipedia.org/wiki/Modbus http://www.simplymodbus.ca/FAQ.htm#Modbus
本實驗的Power Meter通訊Layer 1 採用EIA-485介面
19

## Slide 20
在工業控制場合使用RS232:
在工業控制、電力通訊、智能儀表等領域，通常情況下是採用Serial Port通訊的方式進行數據交換，使用RS232 Port由於工業環境比較複雜，各種電氣設備會在環境中產生較多的EMI電磁干擾，會導致訊號傳輸錯誤。
20

## Slide 21
RS232在工業應用環境的缺點：
傳輸速率有限，不可以過高，一般到幾十kbps就到極限了。
使用信號線和GND與其他設備形成共地模式的通訊，這種共地模式傳輸容易產生干擾，並且抗干擾性能也比較弱。
傳輸距離有限，最多只能通訊幾十米。
連線只能兩點之間進行通訊，不能夠實現多點通訊。
21

## Slide 22
工業控制場合使用RS485:
RS485解決了RS232這些問題，訊號採用差動傳輸方式，可以有效的解決共模干擾問題，最大距離可以到1200米，並且允許多個收發設備接到同一條線上。隨著工業應用設備通訊越來越多，1979年施耐德電氣制定了一個用於工業現場的總線協議Modbus協議，至今仍廣為工業設備使用。
22

## Slide 23
RS485具備以下的特點：
通訊速度快，數據最高傳輸速率為10Mbps以上
傳輸速率最遠可達到1200米左右
線上允許掛多個收發器，從現有的RS485晶片來看，有可以掛32、64、128、256等不同個設備的驅動器
採用電壓差動接收，因此具有抑制共模干擾的能力
RS-485採用半雙工工作方式
23

## Slide 24
Modbus 是​一種​需求-​回應​協定，​採用​主​從​架構​實作​而​成
24

## Slide 25
1 Master device to multi-slave device.
25
Power Meter
Temerature Sensor
Humidity Sensor

## Slide 26
Modbus Frame Format
26

## Slide 27
Modbus Read Input Registers指令
27
參考 http://www.simplymodbus.ca/FC04.htm

## Slide 28
Power Meter回應的封包
28

## Slide 29
Power Meter Modbus Spec
29

## Slide 30
Modbus RTU測試軟體功能
30

## Slide 31
Modbus RTU測試軟體功能
觀察Power Meter RS485收發封包是否正常
手動輸入測試指令,例如Power Meter讀取電壓,確認指令是否正確
測試設備傳輸速率,9600bps至115200bps
測試最大傳輸距離,及是否受到干擾
31

## Slide 32
32
Power Meter
Raspberry pi
Computer
MODBUS
MODBUS
RS485
RS485
通訊架構
使用Modbus RTU查看RS485通訊內容
AB兩條通訊線並接

## Slide 33
NODE RED程式設計
33
Notes: 33

## Slide 34
[{"id":"c83a3d90.1abd6","type":"inject","z":"b8a1d0c1.affd3","name":"","topic":"","payload":"","payloadType":"date","repeat":"","crontab":"","once":true,"x":130,"y":100,"wires":[["44d2d7.8f12ad28"]]},{"id":"44d2d7.8f12ad28","type":"function","z":"b8a1d0c1.affd3","name":"first step initial all global variable to 0","func":"//global variable define\nvar power_meter_data=\n{\n voltage:0,\n ampere:0,\n watt:0,\n PF:0,\n id:\"power_meter_data\",\n rs485_online:0\n};\nglobal.set(\"power_meter_data\",power_meter_data);\nreturn power_meter_data;","outputs":1,"noerr":0,"x":400,"y":100,"wires":[[]]},{"id":"465f0c3c.060824","type":"comment","z":"b8a1d0c1.affd3","name":"開機初始值","info":"","x":120,"y":40,"wires":[]}]
第一部分code:

## Slide 35
35
Initial Value Settings
Notes: 35

## Slide 36
在Function node輸入以下
//global variable define
var power_meter_data=
{
  voltage:0,
  ampere:0,
  watt:0,
  PF:0,
  id:"power_meter_data",
  rs485_online:0
};
global.set("power_meter_data",power_meter_data);
return power_meter_data;
36

## Slide 37
[{"id":"9a4b18a4.d0dc68","type":"inject","z":"b8a1d0c1.affd3","name":"","topic":"","payload":"","payloadType":"date","repeat":"1","crontab":"","once":false,"onceDelay":"","x":130,"y":440,"wires":[["e8697ad2.7c3bc8"]]},{"id":"6751744b.1719bc","type":"debug","z":"b8a1d0c1.affd3","name":"build object msg","active":true,"tosidebar":true,"console":false,"tostatus":false,"complete":"true","targetType":"full","x":600,"y":440,"wires":[]},{"id":"e8697ad2.7c3bc8","type":"function","z":"b8a1d0c1.affd3","name":"build object","func":"var power_meter_data=global.get(\"power_meter_data\");\n//if rs485 online then save data,else fill 0 to data\nif(power_meter_data.rs485_online===1)\n{\n msg.payload = \n {\n \"voltage\":power_meter_data.voltage,\n \"ampere\":power_meter_data.ampere,\n \"watt\":power_meter_data.watt,\n \"powerfactor\":power_meter_data.PF,\n \"rs485_online\":power_meter_data.rs485_online\n };\n}\nelse\n{\n msg.payload = \n {\n \"voltage\":0,\n \"ampere\":0,\n \"watt\":0,\n \"powerfactor\":0,\n \"rs485_online\":power_meter_data.rs485_online\n };\n}\npower_meter_data.rs485_online=0; //clear for next rs485 online test\nglobal.set(\"power_meter_data\",power_meter_data);\n\nreturn msg;","outputs":1,"noerr":0,"x":310,"y":440,"wires":[["cd6248af.0e3da8","6751744b.1719bc","2afdf849.3bac08"]]},{"id":"e63e3e0b.1912a","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":1,"width":0,"height":0,"name":"","label":"voltage","format":"{{msg.payload}} V","layout":"row-spread","x":620,"y":620,"wires":[]},{"id":"a1179e9d.6f7b4","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":3,"width":0,"height":0,"name":"","label":"ampere","format":"{{msg.payload}} A","layout":"row-spread","x":600,"y":700,"wires":[]},{"id":"d6539b23.1ddc78","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":5,"width":0,"height":0,"name":"","label":"watt","format":"{{msg.payload}} W","layout":"row-spread","x":590,"y":780,"wires":[]},{"id":"6394562a.3d3ba8","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":7,"width":0,"height":0,"name":"","label":"Power Factor","format":"{{msg.payload}} %","layout":"row-spread","x":590,"y":880,"wires":[]},{"id":"69b2fbe3.ffaad4","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":2,"width":0,"height":0,"label":"voltage_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"130","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":650,"y":580,"wires":[[]]},{"id":"10d64ad.f5cd1b5","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":4,"width":0,"height":0,"label":"ampere_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":620,"y":660,"wires":[[]]},{"id":"7fca402f.6c0c3","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":6,"width":0,"height":0,"label":"watt_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":610,"y":740,"wires":[[]]},{"id":"7104ea20.16ded4","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":8,"width":0,"height":0,"label":"Power Factor trend","chartType":"horizontalBar","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"1","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":610,"y":820,"wires":[[]]},{"id":"2afdf849.3bac08","type":"function","z":"b8a1d0c1.affd3","name":"dashboard object","func":"var dashboard_voltage={payload:msg.payload.voltage};\nvar dashboard_ampere={payload:msg.payload.ampere};\nvar dashboard_watt={payload:msg.payload.watt};\nvar dashboard_powerfactor={payload:msg.payload.powerfactor};\nvar dashboard_rs485_online={payload:msg.payload.rs485_online};\n\nreturn [dashboard_voltage,dashboard_ampere,dashboard_watt,dashboard_powerfactor,dashboard_rs485_online]","outputs":5,"noerr":0,"x":370,"y":600,"wires":[["e63e3e0b.1912a","69b2fbe3.ffaad4"],["10d64ad.f5cd1b5","a1179e9d.6f7b4"],["7fca402f.6c0c3","d6539b23.1ddc78"],["7104ea20.16ded4","6394562a.3d3ba8"],[]]},{"id":"82e3d28b.99862","type":"comment","z":"b8a1d0c1.affd3","name":"定期更新儀錶板&電源數據存檔","info":"","x":170,"y":380,"wires":[]},{"id":"e8c539d6.400158","type":"comment","z":"b8a1d0c1.affd3","name":"儀錶板顯示","info":"","x":360,"y":520,"wires":[]},{"id":"99df8896.a3e2f8","type":"ui_group","z":"","name":"meter","tab":"acf230be.ed314","order":1,"disp":true,"width":"6","collapse":false},{"id":"acf230be.ed314","type":"ui_tab","z":"","name":"home","icon":"dashboard","order":1}]
第二部分code:

## Slide 38
38
Modbus Decode
Notes: 38

## Slide 39
39
Modbus Read 編輯
Notes: 39

## Slide 40
40
Modbus Read 編輯
Notes: 40

## Slide 41
在Function node輸入以下
//packet decoder
msg.voltage=msg.payload[0]/10;
msg.ampere=(msg.payload[2]*65535+msg.payload[1])/1000;
msg.watt=(msg.payload[4]*65535+msg.payload[3])/10;
msg.Wh=(msg.payload[6]*65535+msg.payload[5])/1000;
msg.freq=msg.payload[7]/10;
msg.PF=msg.payload[8]/100;
msg.alarm=msg.payload[9];
//save data to global variables
var power_meter_data=global.get("power_meter_data");
power_meter_data.voltage=msg.voltage;
power_meter_data.ampere=msg.ampere;
power_meter_data.watt=msg.watt;
power_meter_data.PF=msg.PF;
power_meter_data.rs485_online=1;
global.set("power_meter_data",power_meter_data);
return power_meter_data
41

## Slide 42
[{"id":"9a4b18a4.d0dc68","type":"inject","z":"b8a1d0c1.affd3","name":"","topic":"","payload":"","payloadType":"date","repeat":"1","crontab":"","once":false,"onceDelay":"","x":130,"y":440,"wires":[["e8697ad2.7c3bc8"]]},{"id":"6751744b.1719bc","type":"debug","z":"b8a1d0c1.affd3","name":"build object msg","active":true,"tosidebar":true,"console":false,"tostatus":false,"complete":"true","targetType":"full","x":600,"y":440,"wires":[]},{"id":"e8697ad2.7c3bc8","type":"function","z":"b8a1d0c1.affd3","name":"build object","func":"var power_meter_data=global.get(\"power_meter_data\");\n//if rs485 online then save data,else fill 0 to data\nif(power_meter_data.rs485_online===1)\n{\n msg.payload = \n {\n \"voltage\":power_meter_data.voltage,\n \"ampere\":power_meter_data.ampere,\n \"watt\":power_meter_data.watt,\n \"powerfactor\":power_meter_data.PF,\n \"rs485_online\":power_meter_data.rs485_online\n };\n}\nelse\n{\n msg.payload = \n {\n \"voltage\":0,\n \"ampere\":0,\n \"watt\":0,\n \"powerfactor\":0,\n \"rs485_online\":power_meter_data.rs485_online\n };\n}\npower_meter_data.rs485_online=0; //clear for next rs485 online test\nglobal.set(\"power_meter_data\",power_meter_data);\n\nreturn msg;","outputs":1,"noerr":0,"x":310,"y":440,"wires":[["cd6248af.0e3da8","6751744b.1719bc","2afdf849.3bac08"]]},{"id":"e63e3e0b.1912a","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":1,"width":0,"height":0,"name":"","label":"voltage","format":"{{msg.payload}} V","layout":"row-spread","x":620,"y":620,"wires":[]},{"id":"a1179e9d.6f7b4","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":3,"width":0,"height":0,"name":"","label":"ampere","format":"{{msg.payload}} A","layout":"row-spread","x":600,"y":700,"wires":[]},{"id":"d6539b23.1ddc78","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":5,"width":0,"height":0,"name":"","label":"watt","format":"{{msg.payload}} W","layout":"row-spread","x":590,"y":780,"wires":[]},{"id":"6394562a.3d3ba8","type":"ui_text","z":"b8a1d0c1.affd3","group":"99df8896.a3e2f8","order":7,"width":0,"height":0,"name":"","label":"Power Factor","format":"{{msg.payload}} %","layout":"row-spread","x":590,"y":880,"wires":[]},{"id":"69b2fbe3.ffaad4","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":2,"width":0,"height":0,"label":"voltage_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"130","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":650,"y":580,"wires":[[]]},{"id":"10d64ad.f5cd1b5","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":4,"width":0,"height":0,"label":"ampere_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":620,"y":660,"wires":[[]]},{"id":"7fca402f.6c0c3","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":6,"width":0,"height":0,"label":"watt_trend","chartType":"line","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":610,"y":740,"wires":[[]]},{"id":"7104ea20.16ded4","type":"ui_chart","z":"b8a1d0c1.affd3","name":"","group":"99df8896.a3e2f8","order":8,"width":0,"height":0,"label":"Power Factor trend","chartType":"horizontalBar","legend":"false","xformat":"HH:mm:ss","interpolate":"linear","nodata":"","dot":false,"ymin":"0","ymax":"1","removeOlder":"3","removeOlderPoints":"","removeOlderUnit":"60","cutout":0,"useOneColor":false,"colors":["#1f77b4","#aec7e8","#ff7f0e","#2ca02c","#98df8a","#d62728","#ff9896","#9467bd","#c5b0d5"],"useOldStyle":false,"outputs":1,"x":610,"y":820,"wires":[[]]},{"id":"2afdf849.3bac08","type":"function","z":"b8a1d0c1.affd3","name":"dashboard object","func":"var dashboard_voltage={payload:msg.payload.voltage};\nvar dashboard_ampere={payload:msg.payload.ampere};\nvar dashboard_watt={payload:msg.payload.watt};\nvar dashboard_powerfactor={payload:msg.payload.powerfactor};\nvar dashboard_rs485_online={payload:msg.payload.rs485_online};\n\nreturn [dashboard_voltage,dashboard_ampere,dashboard_watt,dashboard_powerfactor,dashboard_rs485_online]","outputs":5,"noerr":0,"x":370,"y":600,"wires":[["e63e3e0b.1912a","69b2fbe3.ffaad4"],["10d64ad.f5cd1b5","a1179e9d.6f7b4"],["7fca402f.6c0c3","d6539b23.1ddc78"],["7104ea20.16ded4","6394562a.3d3ba8"],[]]},{"id":"82e3d28b.99862","type":"comment","z":"b8a1d0c1.affd3","name":"定期更新儀錶板&電源數據存檔","info":"","x":170,"y":380,"wires":[]},{"id":"e8c539d6.400158","type":"comment","z":"b8a1d0c1.affd3","name":"儀錶板顯示","info":"","x":360,"y":520,"wires":[]},{"id":"99df8896.a3e2f8","type":"ui_group","z":"","name":"meter","tab":"acf230be.ed314","order":1,"disp":true,"width":"6","collapse":false},{"id":"acf230be.ed314","type":"ui_tab","z":"","name":"home","icon":"dashboard","order":1}]
第三部分code:

## Slide 43
43
Dashboard
Notes: 43

## Slide 44
在Function node (build object)輸入以下
var power_meter_data=global.get("power_meter_data");
//if rs485 online then save data,else fill 0 to data
if(power_meter_data.rs485_online===1){
msg.payload =
  {
    "voltage":power_meter_data.voltage,
    "ampere":power_meter_data.ampere,
    "watt":power_meter_data.watt,
    "powerfactor":power_meter_data.PF,
    "rs485_online":power_meter_data.rs485_online
  };
}
else{
msg.payload =
{
  "voltage":0,
  "ampere":0,
  "watt":0,
  "powerfactor":0,
  "rs485_online":power_meter_data.rs485_online
  };
}
power_meter_data.rs485_online=0;
//clear for next rs485 online test
global.set("power_meter_data",power_meter_data);
return msg;
44

## Slide 45
在Function node (dashboard object)輸入以下
var dashboard_voltage={payload:msg.payload.voltage};
var dashboard_ampere={payload:msg.payload.ampere};
var dashboard_watt={payload:msg.payload.watt};
var dashboard_powerfactor={payload:msg.payload.powerfactor};
var dashboard_rs485_online={payload:msg.payload.rs485_online};
return [dashboard_voltage,dashboard_ampere,
dashboard_watt,dashboard_powerfactor,dashboard_rs485_online]
45

## Slide 46
46
時間範圍
設為線圖
圖標題
電壓(電流)範圍
chart顯示的區域

## Slide 47
47
電壓數值,及單位
Label顯示”voltage”

## Slide 48
48

## Slide 49
[{"id":"cd6248af.0e3da8","type":"function","z":"b8a1d0c1.affd3","name":"add data time stamp","func":"var now = new Date(); \nvar year = now.getFullYear();\nvar month = now.getMonth()+1; \nvar day = now.getDate();\nvar hour = now.getHours();\nvar minute = now.getMinutes();\nvar second = now.getSeconds(); \nif(month.toString().length == 1) \n{\n month = '0'+month;\n}\nif(day.toString().length == 1) \n{\n day = '0'+day;\n} \nif(hour.toString().length == 1) \n{\n hour = '0'+hour;\n}\nif(minute.toString().length == 1) \n{\n minute = '0'+minute;\n}\nif(second.toString().length == 1) \n{\n second = '0'+second;\n} \n\n//csv file path\nmsg.filename='/home/pi/Desktop/PowerMeter/PowerMeter_'+year+month+day+ '.csv';\nmsg.payload.timestamp =hour+':'+minute+':'+second;\n\nif((hour=='00')&&(minute=='00')&&((second<='00'))) //cross day\n{\n return [null,msg]; //2th output csv title field\n}\nelse //other time\n{\n return [msg,null]; //1st output csv data field\n}","outputs":"2","noerr":0,"x":180,"y":1020,"wires":[["be4fc5d3.0f2d28"],["96bea81d.ff1bf8"]]},{"id":"be4fc5d3.0f2d28","type":"csv","z":"b8a1d0c1.affd3","name":"紀錄每秒數值","sep":",","hdrin":true,"hdrout":false,"multi":"one","ret":"\\n","temp":"timestamp,voltage,ampere,watt,powerfactor,rs485_online","skip":0,"strings":true,"x":460,"y":1000,"wires":[["263bccab.06b504","d4d0c8c8.d71768"]]},{"id":"263bccab.06b504","type":"file","z":"b8a1d0c1.affd3","name":"file saved at tc_data","filename":"","appendNewline":false,"createDir":true,"overwriteFile":"false","x":820,"y":1000,"wires":[[]]},{"id":"96bea81d.ff1bf8","type":"csv","z":"b8a1d0c1.affd3","name":"跨零時填標題","sep":",","hdrin":false,"hdrout":true,"multi":"one","ret":"\\n","temp":"timestamp,voltage,ampere,watt,powerfactor,rs485_online","skip":0,"strings":true,"x":460,"y":1040,"wires":[["263bccab.06b504","d4d0c8c8.d71768"]]},{"id":"d4d0c8c8.d71768","type":"debug","z":"b8a1d0c1.affd3","d":true,"name":"","active":true,"tosidebar":true,"console":false,"tostatus":false,"complete":"payload","targetType":"msg","x":810,"y":1080,"wires":[]},{"id":"99cd33e8.3e0df","type":"comment","z":"b8a1d0c1.affd3","name":"存檔","info":"","x":170,"y":960,"wires":[]}]
第四部分code:

## Slide 51
在Function node (dashboard object)輸入以下
var now = new Date();
var year = now.getFullYear();
var month = now.getMonth()+1;
var day = now.getDate();
var hour = now.getHours();
var minute = now.getMinutes();
var second = now.getSeconds();
if(month.toString().length == 1)
{ month = '0'+month;}
if(day.toString().length == 1)
{ day = '0'+day;}
if(hour.toString().length == 1)
{ hour = '0'+hour;}
if(minute.toString().length == 1)
{ minute = '0'+minute;}
if(second.toString().length == 1)
{ second = '0'+second;}
//csv file path
msg.filename='/home/pi/Desktop/PowerMeter/PowerMeter_'+year+month+day+ '.csv';
msg.payload.timestamp =hour+':'+minute+':'+second;
if((hour=='00')&&(minute=='00')&&((second<='00')))
//cross day
{ return [null,msg];
//2th output csv title field
}else //other time{ return [msg,null]; //1st output csv data field}
51
存檔路徑,linux檔案目錄使用/ windows使用\

## Slide 52
Email node:
設定超過用電量,發送email通知使用者
可傳送任何形態的參數
52

## Slide 53
53

## Slide 54
54
Gmail使用者須做以下設定

## Slide 55
55
習題
Notes: 55

## Slide 56
56
Power Meter
Raspberry pi
Desktop Computer
Internet
MQTT
MODBUS
MQTT
RS485
習題1:
在家庭環境下,
使用網路基礎設施
傳遞訊息
用電腦NODE RED的
DASHBOARD顯示用電數據

## Slide 57
57
Reference
Notes: 57

## Slide 58
Node js語法英文參考(推薦)
https://www.w3schools.com/js/default.asp
Node js語法中文參考
https://dca.gitbooks.io/nodejs-tw-wiki-book/content/index.html
Node-red官方GitHub
https://github.com/node-red
58

## Slide 59
Thank you 
59
Notes: 59